## Seamless Tube
Safe Working Pressure and Bursting Pressure per ASME B31.1-2007
Step #1 | 0.3725 | Input outside diameter (in)
Step #2 | 0.025 | Input wall thickness (in)
Step #3 | 10000 | Input maximum allowable stress (psi) from table below
Step #4 | 46000 | Input minimum tensile strength (psi) from table below
| 1418.4397 | Maximum allowable working pressure (psi) at temp
| 6174.4966 | Bursting pressure (psi)
For seamless tube:
Maximum allowable stress in psi at operating temperature, in °F, not exceeding1
| ASTM Spec No. | Alloy No. | Temper | Minimum Tensile, psi | Minimum Yield, psi | -20 to 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 700 | 750
| B42/ B75 | C10200 C12000 C12200 | Annealed | 30000 | 9000 | 6000 | 5100 | 4900 | 4800 | 4700 | 4000 | 3000
|  | C10200 C12000 C12200 | Drawn | 36000 | 30000 | 10300 | 10300 | 10300 | 10300 | 10000 | 9700 | 9400
|  | C10200 C12000 C12200 | Hard | 45000 | 40000 | 12900 | 12900 | 12900 | 12500 | 12500 | 11800 | 4300
| B43 | C23000 | Annealed | 40000 | 12000 | 8000 | 8000 | 8000 | 8000 | 8000 | 7000 | 5000 | 2000
|  | C23000 | Drawn | 44000 | 18000 | 8000 | 8000 | 8000 | 8000 | 8000 | 7000 | 5000 | 2000
| B68 | C10200 C12000 C12200 | Annealed | 30000 | 9000 | 6000 | 5100 | 4900 | 4800 | 4700 | 4000 | 3000
| B88 | C10200 C12000 C12200 | Annealed | 30000 | 9000 | 6000 | 5100 | 4900 | 4800 | 4700 | 4000 | 3000
|  | C10200 C12000 C12200 | Drawn | 36000 | 30000 | 10300 | 10300 | 10300 | 10300 | 10000 | 9700 | 9400
| B111 | C10200 C12000 C12200 | Light Drawn | 36000 | 30000 | 10300 | 10300 | 10300 | 10300 | 10000 | 9700 | 9400
|  | C10200 C12000 C12200 | Hard | 45000 | 40000 | 12900 | 12900 | 12900 | 12500 | 12500 | 11800 | 4300
| B111 | C23000 | Annealed | 40000 | 12000 | 8000 | 8000 | 8000 | 8000 | 8000 | 7000 | 5000 | 2000
|  | C44300 | Annealed | 45000 | 15000 | 10000 | 10000 | 10000 | 10000 | 10000 | 9800 | 3500 | 2000
|  | C70600 | Annealed | 40000 | 15000 | 10000 | 9700 | 9500 | 9300 | 9000 | 8800 | 8700 | 8500 | 8000 | 7000 | 6000
|  | C71500 | Annealed | 52000 | 18000 | 12000 | 11600 | 11300 | 11000 | 10800 | 10500 | 10300 | 10100 | 9900 | 9800 | 9600 | 9500 | 9400
| B280 | C12200 | Annealed | 30000 | 9000 | 6000 | 5100 | 4800 | 4800 | 4700 | 4000 | 3000
|  | C12200 | Drawn | 36000 | 30000 | 10300 | 10300 | 10300 | 10300 | 10,00 | 9700 | 9400
| B466 | C70600 | Annealed | 38000 | 13000 | 8700 | 8400 | 8200 | 8000 | 7800 | 7700 | 7500 | 7400 | 7300 | 7000 | 6000
|  | C71500 | Annealed | 50000 | 18000 | 12000 | 11600 | 11300 | 11000 | 10800 | 10500 | 10300 | 10100 | 9900 | 9800 | 9600
1) Maximum allowable stress values taken from ASME B 31.1 Appendix A, Table A-6

## Welded Copper Nickel
Safe Working Pressure and Bursting Pressure per ASME B31-2007
Step #1 | 0.625 | Input outside diameter (in)
Step #2 | 0.049 | Input wall thickness (in)
Step #3 | 8500 | Input maximum allowable stress (psi) from table below
Step #4 | 40000 | Input minimum tensile strength (psi) from table below
| 1421.987 | Maximum allowable working pressure (psi) at temp
| 6272 | Bursting pressure (psi)
For welded tube:
Maximum allowable stress in psi at operating temperature, in °F, not exceeding1
| ASTM Spec No. | Alloy No. | Temper | Minimum Tensile, ksi | Minimum Yield, ksi | -20 to 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 700 | 750
| B467 | C70600 | Annealed | 40000 | 15000 | 8500 | 8300 | 8100 | 7900 | 7700 | 7500 | 7400 | 7200 | 6300 | 5700 | 4300
| B476 | C71500 | Annealed | 50000 | 20000 | 11300 | 10900 | 10700 | 10400 | 10200 | 10000 | 9700 | 9600 | 9400 | 9200 | 9100
1) Maximum allowable stress values taken from ASME B 31.1 Appendix A, Table A-6

## Aluminum
Safe Working Pressure and Bursting Pressure per ASME B31.1-2007
Step #1 | 0.375 | Input outside diameter (in)
Step #2 | 0.025 | Input wall thickness (in)
Step #3 | 3400 | Input maximum allowable stress (psi) from table below
Step #4 | 14000 | Input minimum tensile strength (psi) from table below
| 478.8732 | Maximum allowable working pressure (psi) at temp
| 1866.6667 | Bursting pressure (psi)
For Aluminum Tube:
Maximum allowable stress in psi at operating temperature, in °F, not exceeding1
| ASTM Spec No. | Alloy No. | Temper | Minimum Tensile, psi | Minimum Yield, psi | -20 to 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 700 | 750
| B210 | A93003 | O Annealed | 14000 | 5000 | 3400 | 3400 | 34000 | 3000 | 2400 | 1800 | 1400
|  | A93003 | H14 1/2 hard | 20000 | 17000 | 5700 | 5700 | 5700 | 4900 | 4300 | 3000 | 2300
| B234 | A93003 | H14 1/2 hard | 20000 | 17000 | 5700 | 5700 | 5700 | 4900 | 4300 | 3000 | 2400
| B241 | A93003 | O Annealed | 14000 | 5000 | 3400 | 3400 | 3400 | 3000 | 2400 | 1800 | 1400
|  | A93003 | H18 Hard | 27000 | 24000 | 7800 | 7800 | 7700 | 6300 | 5400 | 3500 | 2500
1) Maximum allowable stress values taken from ASME B 31.1 Appendix A, Table A-7